PERMIT NUMBER__________________						REGION:

DATE________________________						COUNTY:  FORD

PROPERTY OWNER _________________________			INSPECTOR’S NAME______________________

INSTALLATION CONTRACTOR_________________________________________________________

(NAME)						(LICENSE NUMBER)

LOCATION OF SYSTEM FROM DWELLING_______________LOCATION OF ALARMS_______ (High Water) _______(ATU)

GALLONS TO BE TREATED PER DAY ___________ SEPTIC TANK_____SIZE______ BRAND __________ IL #_______

(OR)  AERATION TANK ______ 	BRAND_________________ MODEL/SIZE_______________

SEPTIC/AERATON TANK WITHIN ½” OF LEVEL 						YES		NO

ELEVATION OF SYSTEM (TANK)								YES		NO

PUMP CHAMBER SIZE _________   BRAND_____________

PUMP DOSING CHAMBER (PUMP TANK) (MIN OF 500 GAL or 1 DAY CAPACITY)		YES		NO

ANSI OR NSF SEALS APPLIED 								YES		NO

EFFLUENT FILTER(S) INSTALLED								YES		NO

EFFLUENT      /       TURBINE      PUMP BRAND____________PUMP SIZE _________ DOSE VOLUME__________

ANTI-SIPHON HOLE OR CONTROL MEASURE ON DOSING CHAMBER			YES		NO

SUBMERSIBLE EFFLUENT PUMP WITH ON/OFF DOSING CONTROLS			YES		NO

*RECOMMENDED ELAPSED TIME METER AND CYCLE COUNTER			YES		NO

SITE HAS LESS THAN 10% SLOPE								YES		NO

SITE DRAINAGE FOR DIVERSION OVER SUBSURFACE SYSTEM				YES		NO

SUPPLY LINE - MANIFOLD LINE (REQUIRED:  2” SCHEDULE 40) ASTM________		YES		NO

BALL VALVES INSTALLED ON EACH DISTRIBUTION LINE (ACHIEVE 3’ SQUIRT HEIGHT)	YES		NO

VALVE HOUSED IN COMPARTMENT AND EASILY ACCESSIBLE FOR ADJUSTMENT		YES		NO

LENGTH OF EACH TRENCH (MAX 70’) ___________ NUMBER OF ROWS__________TOTAL LENGTH _________

MINIMUM OF 12 INCHES OF VERTICAL SEPARATION FROM BOTTOM OF

TRENCH TO ANY LIMITING LAYER OR SEASONAL HIGH WATER TABLE			YES		NO

SPACING FOR TRENCHES (MIN 5’ CENTER-TO-CENTER)					YES		NO

TRENCH DEPTH (8’ – 12” TYPICAL – MAX 18”)						YES		NO

MINIMUM PRODUCT HEIGHT 8”								YES		NO

TRENCH WIDTH: REQUIRED 3’								YES		NO

CHAMBER SIZE/BRAND__________________EZ FLOW __________  GRAVEL ________ EPS AGGREGATE _____________

OTHER___________________________________________________

DISTRIBUTION LATERALS (REQUIRED 1 ½” SCHEDULE 40) ASTM__________ 		YES		NO

SCHEDULE 40;  90’ BEND TURNED UP WITH THREADED END ON DISTAL END OF LINE	YES		NO

HOLE DIMINSION (TYPICALLY 5/32”) DRILLED EVERY 5 FEET ON THE TOP OF LINE		YES		NO

1 - 5/32” HOLE DRILLED ON BOTTOM OF EACH END OF LINE (1-2’) FOR DRAINAGE	YES		NO

END CAPS INSTALLED TO PREVENT HYDRAULIC MOVEMENT				YES		NO

REQUIRED MIN 2’ EARTHEN DAM ON FRONT AND BACK OF TRENCHES			YES		NO

FOR PEA GRAVEL SUBSURFACE SYSTEM - REQUIRED ORIFACE SHIELDS			YES		NO

3’ CHECK FOR SQUIRT HEIGHT OF SYSTEM AFTER INSTALLED				YES		NO

IDPH LLP PSD SYSTEM WORKSHEET USED FOR DESIGN					YES		NO

COMMENTS: ________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________